## Archibus
| Assessment Item | CSI ID | Includes | Condition Value | CSI Rating Description
A. SUBSTRUCTURE | Standard Foundations | A1010 | Continuous wall footings, strip footings, isolated column footings, grade beams, combined footings, strap footings, mat foundations, below-grade foundation/stem walls, driven piles, drilled piers, caissons, micropiles, helical piles, integral reinforcing steel, anchor bolts, embedded plates, base plates, bearing soil preparation, foundation insulation, vapor barriers, and dampproofing integral to footing assembly. | New | Foundation shows no cracking, settlement, moisture intrusion, or movement.
|  |  |  | Routine Maintenance | Minor surface wear or hairline cracks without displacement or moisture concerns.
|  |  |  | Minor Repair | Localized cracks, slight movement, or minor moisture staining requiring repair but not structural.
|  |  |  | Major Repair | Settlement, heave, or displaced cracks causing separation or leaks indicating structural issues.
|  |  |  | Replacement | Severe cracking, major displacement, or structural failure requiring urgent replacement.
| Basement Walls | A2010 | Reinforced cast-in-place or precast concrete basement walls, masonry foundation or retaining walls forming subgrade enclosures, integral reinforcing steel, ties, bond beams, embedded plates, insulation, vapor barriers, dampproofing, waterproofing systems, perimeter/footing drains, drainage mats, collector pipes, protective boards, sumps, sealants, joints, waterstops, through-wall flashings, and penetrations. | New | Walls are plumb, crack-free, dry, and stable with no bowing or leaks.
|  |  |  | Routine Maintenance | Minor wear or small hairline cracks with no moisture intrusion.
|  |  |  | Minor Repair | Local cracking, light staining, or small leaks needing repair to maintain performance.
|  |  |  | Major Repair | Bowing, rotation, major cracking, or chronic leakage affecting structural integrity.
|  |  |  | Replacement | Severe movement, major leakage, or instability requiring wall replacement.
| Slab-on-Grade | A4010 | Reinforced or unreinforced concrete slabs bearing on soil or compacted fill, subbase preparation, fine grading, mud slabs, vapor retarders, waterproofing membranes, insulation integral to slab assembly, expansion joints, control joints, sawcuts, integral curbs or bases, finished concrete surfaces, embedded reinforcement, embedded radiant heating or snow-melt piping, slabs in mechanical/utility/service spaces. | New | Slab is level, crack-free, dry, and fully intact with functional joints.
|  |  |  | Routine Maintenance | Small shrinkage cracks or light wear with no moisture or movement issues.
|  |  |  | Minor Repair | Local settlement, unevenness, staining, or joint deterioration requiring repair.
|  |  |  | Major Repair | Widespread cracking, heaving, moisture migration, or movement impacting finishes or systems.
|  |  |  | Replacement | Severe failure, major spalling, or compromised subbase requiring replacement.
B. SHELL | Floor Construction | B1010 | Structural framing for elevated floors including beams, girders, joists, trusses, open-web steel joists, composite steel deck systems; cast-in-place, precast, or post-tensioned concrete slabs not bearing on grade; wood joist systems, engineered lumber, plywood/OSB subflooring; fire-rated assemblies, underfloor fireproofing, structural coatings; embedded reinforcement, post-tensioning cables, floor penetrations, openings, access panels. | New | Floor structure shows no deflection, cracking, corrosion, or moisture issues.
|  |  |  | Routine Maintenance | Minor cosmetic cracks or wear; fireproofing or coatings need small touch-ups.
|  |  |  | Minor Repair | Local spalling, exposed rebar, vibration, or dampness requiring repair.
|  |  |  | Major Repair | Major deflection, cracking, corrosion, or leaks reducing structural performance.
|  |  |  | Replacement | Severe structural deterioration or unsafe conditions requiring full replacement.
| Roof Construction | B1020 | Structural roof framing including rafters, trusses, beams, purlins, joists, decking; precast concrete planks, poured-in-place concrete roof slabs; metal roof deck, plywood or OSB sheathing; roof structural bracing and lateral systems; wood and steel framing members; insulation boards attached to roof deck; parapets as structural elements; roof openings, curbs, and structural penetrations for equipment. | New | Roof structure is straight, dry, and free of cracking, corrosion, or deformation.
|  |  |  | Routine Maintenance | Minor oxidation or surface wear with no structural impact or moisture staining.
|  |  |  | Minor Repair | Local corrosion, small cracks, or early moisture staining requiring limited repair.
|  |  |  | Major Repair | Deflection, sagging, corrosion, or leaks affecting roof framing or connections.
|  |  |  | Replacement | Severe deterioration, major deformation, or unsafe structural failure requiring replacement.
| Stair Construction | B1080 | Structural stair framing including steel stringers, concrete stair flights, wood framing, metal pan systems; treads, risers, nosings, and landings integral to stair assembly; stair supports, anchors, brackets, connections to floors or walls; guards, handrails, intermediate rails, rail support posts; stairway fire-resistance features where part of stair assembly; precast concrete stairs and landings; exterior stair structures attached to building. | New | Stairs, supports, treads, and rails are solid, aligned, and damage-free.
|  |  |  | Routine Maintenance | Light wear or slight corrosion with no impact on safety or operation.
|  |  |  | Minor Repair | Local spalling, loose components, or minor deformation requiring repair.
|  |  |  | Major Repair | Significant corrosion, cracked treads, failing rails, or movement affecting safe use.
|  |  |  | Replacement | Severe structural failure, major deformation, or unsafe conditions requiring replacement.
| Exterior WallS | B2010 | Load-bearing and non-load-bearing wall framing, masonry and concrete walls, curtain wall and storefront systems, metal and wood stud framing, exterior sheathing, cladding systems, exterior insulation, weather barriers, air barriers, expansion joints, control joints, sealants, window and door frames as part of wall assembly, parapets, copings, canopies integral to wall system. | New | Exterior walls are intact, watertight, stable, and free of cracking or displacement.
|  |  |  | Routine Maintenance | Minor sealant wear, light cracking, or small finish defects without leakage.
|  |  |  | Minor Repair | Local spalling, sealant failure, minor leaks, or moisture staining needing repair.
|  |  |  | Major Repair | Widespread cracking, delamination, water intrusion, or degraded sheathing.
|  |  |  | Replacement | Severe façade failure, major detachment, or systemic moisture damage requiring replacement.
| Exterior Windows | B2020 | Fixed and operable window units including frames, sash, glazing, insulated glass units, low-E and specialty coatings, weather-stripping, gaskets, sealants, integral screens, muntins, mullions, hardware and operators for operable units, anchors and mounting systems, accessory items like window wells for basement windows, security glazing in windows. | New | Windows operate smoothly with intact frames, glazing, seals, and hardware.
|  |  |  | Routine Maintenance | Small gasket wear, slight finish aging, or minor operation resistance.
|  |  |  | Minor Repair | Local seal failure, light corrosion, early fogging, or small hardware issues.
|  |  |  | Major Repair | Widespread fogging, warped frames, failed seals, or leaks affecting performance.
|  |  |  | Replacement | Major frame failure, pervasive leaks, or glazing instability requiring full replacement.
| Exterior Doors | B2050 | Door leaves, frames, thresholds, weather-stripping, hinges, locksets, closers, panic hardware, automatic door operators, overhead doors and operators, storefront entrance systems, revolving doors, sliding and folding doors, specialty exterior doors, hardware and accessories, door glazing integral to door assembly, seals and gaskets, kick plates and protective trim integral to door unit. | New | Exterior doors, frames, and seals are aligned, fully functional, and free of corrosion, warping, or air/water infiltration.
|  |  |  | Routine Maintenance | Minor finish wear or slight sealant aging with no leaks or operational issues.
|  |  |  | Minor Repair | Local corrosion, worn seals, misalignment, sticking doors, or minor leakage requiring repair.
|  |  |  | Major Repair | Significant corrosion, warping, failed seals, or persistent leakage affecting security or performance.
|  |  |  | Replacement | Severe deterioration, major deformation, or non-functional hardware requiring full door replacement.
| Roofing | B3010 | Roof membranes including built-up, modified bitumen, single-ply, fluid-applied; base and cap sheets; insulation above deck; roof flashing at walls, penetrations, edges; counterflashing and reglets; roof drains, scuppers, overflow drains; gravel stops, edge metal, fascia; roof expansion joints; walkway pads; pitch pans; cant strips; temporary roof protection during construction. | New | Roofing and flashings are intact with no punctures, open seams, moisture intrusion, or drainage issues.
|  |  |  | Routine Maintenance | Minor surface wear, small blisters, or light sealant aging with no leaks.
|  |  |  | Minor Repair | Local membrane damage, minor leaks, deteriorated flashings, or ponding needing repair.
|  |  |  | Major Repair | Widespread leaks, wet insulation, major flashing failure, or extensive membrane deterioration.
|  |  |  | Replacement | Severe membrane failure, saturated insulation, or structural impact requiring full roof replacement.
| Roof Openings | B3060 | Roof access components including roof hatches, ship ladders, associated curbs; daylighting and glazed roof units including skylights, tubular daylight devices, roof monitors with glazing; smoke and heat vents including gravity vents, automatic smoke vents, curb structures; roof penetrations and curbs for HVAC, plumbing, electrical, exhaust; penetration flashings, boots, pitch pans integral to opening; localized structural framing integral to opening. | New | Roof hatches, skylights, curbs, and penetrations are fully sealed, damage-free, and leak-free with proper operation.
|  |  |  | Routine Maintenance | Minor sealant aging, slight wear, or small hardware stiffness with no leaks.
|  |  |  | Minor Repair | Local seal failure, glazing issues, small leaks, or minor hardware problems needing repair.
|  |  |  | Major Repair | Cracked glazing, leaking curbs, failing seals, or damaged mechanisms reducing weather protection.
|  |  |  | Replacement | Severe glazing failure, structural curb issues, or inoperable hatches requiring full replacement.
C. INTERIORS | Interior Walls & Windows | C1010 | Non-load-bearing interior partitions including metal stud, wood stud, masonry; gypsum board assemblies, lath and plaster systems; moveable and demountable partitions; fire-rated wall assemblies, shaft walls, smoke partitions; interior glazing systems, borrowed lights, interior windows; door frames integrated into partition systems; wall blocking, backing, and reinforcement; control joints, expansion joints, corner bead, trim accessories. | New | Interior partitions and glazing are intact, stable, clean, and free of cracking, moisture staining, or damage.
|  |  |  | Routine Maintenance | Minor finish wear, small cracks, or slight joint separation with no structural impact.
|  |  |  | Minor Repair | Local cracking, damaged gypsum, loose glazing stops, or minor moisture spots requiring repair.
|  |  |  | Major Repair | Significant cracking, moisture damage, bowed partitions, or compromised fire/smoke barriers.
|  |  |  | Replacement | Severe wall failure, major moisture damage, delamination, or structural issues requiring replacement.
| Interior Doors | C1030 | Interior door leaves, door frames, thresholds, hinges, locksets, latches, closers, stops, kick plates, push/pull plates, vision panels and glazing in doors, sliding and folding door hardware, pocket door tracks and frames, fire-rated doors and hardware, smoke doors, sound-rated doors, specialty doors, weatherstripping for conditioned space separation, coordinator hardware for pairs. | New | Interior doors and frames operate smoothly, are aligned, and show no damage, warping, or hardware issues.
|  |  |  | Routine Maintenance | Minor finish wear or light hardware looseness with no impact on door function.
|  |  |  | Minor Repair | Local delamination, sticking, small hardware failures, or minor frame damage requiring repair.
|  |  |  | Major Repair | Major warping, damaged frames, failing hardware, or compromised fire-rated assemblies.
|  |  |  | Replacement | Severe door or frame damage, inoperable hardware, or structural failure requiring full replacement.
| Interior Specialties | C1090 | Toilet partitions and urinal screens, toilet accessories like grab bars, paper dispensers, soap dispensers, mirrors; corner guards, wall protection, crash rails; demountable and folding partitions; operable partitions and acoustic dividers; chalkboards, whiteboards, tackboards; display cases and bulletin boards; signage systems; fire extinguisher cabinets; mail collection units; lockers and storage units; cubicle curtains and tracks. | New | Interior specialties like lockers, wall guards, and accessories are secure, undamaged, and fully functional.
|  |  |  | Routine Maintenance | Minor scratches, light wear, or small fastener tightening needed with no performance issues.
|  |  |  | Minor Repair | Local dents, loose anchors, damaged accessories, or moderate wear needing repair.
|  |  |  | Major Repair | Widespread damage, loose or failing attachments, or deterioration affecting usability or safety.
|  |  |  | Replacement | Severe damage, structural failure, or non-functional specialty items requiring replacement.
| Wall Finishes | C2010 | Paint, stain, clear finishes; wallcovering, fabric wall systems, vinyl wall covering; ceramic tile, quarry tile, porcelain tile; stone veneer, thin-set stone, panels; wood paneling, wainscoting; FRP panels, plastic laminate; acoustical wall panels; specialized coatings like epoxy, antimicrobial; decorative plaster, textured finishes; metal panels as finish material; glass tile, mosaic tile; grout, sealants, adhesives for finishes. | New | Wall finishes are clean, intact, and free of cracking, staining, delamination, or moisture damage.
|  |  |  | Routine Maintenance | Minor scuffs, small cracks, or light finish wear with no substrate issues.
|  |  |  | Minor Repair | Local peeling, cracked tile, damaged grout, or minor moisture staining requiring repair.
|  |  |  | Major Repair | Widespread finish failure, staining, substrate deterioration, or moisture-related damage.
|  |  |  | Replacement | Extensive failure, severe moisture damage, or compromised substrates requiring full replacement.
| Floor Finishes | C2030 | Resilient flooring including VCT, LVT, sheet vinyl, linoleum, rubber flooring; ceramic tile, porcelain tile, quarry tile, stone tile; carpet and carpet tile, pad and underlayment; wood flooring, engineered wood, bamboo; terrazzo, polished concrete, stained concrete; raised access flooring systems; epoxy coatings, urethane toppings; athletic flooring, rubber sports surfaces; base, transitions, edge trim integral to floor finish; floor sealants and adhesives. | New | Floor finishes are smooth, secure, undamaged, and free of wear, cracking, or moisture issues.
|  |  |  | Routine Maintenance | Light wear, minor scratches, or small aging areas with no safety concerns.
|  |  |  | Minor Repair | Local delamination, loose tiles, damaged transitions, or small moisture issues requiring repair.
|  |  |  | Major Repair | Major wear, hollow tiles, widespread delamination, or moisture damage impairing safety.
|  |  |  | Replacement | Severe failure, extensive water damage, or large-area delamination requiring full replacement.
| Ceiling Finishes | C2050 | Suspended acoustic ceiling tile and grid systems, gypsum board ceilings on furring or framing, plaster ceilings, wood ceilings including planks and panels, metal panel ceilings, acoustical clouds and baffles, specialty ceiling systems, integrated lighting/ceiling systems, access panels in ceilings, ceiling trim and edge details, suspension systems and hangers, ceiling insulation above finish, painted or finished ceiling surfaces. | New | Ceilings are level, clean, secure, and free of staining, sagging, cracks, or loose grid components.
|  |  |  | Routine Maintenance | Minor scuffs, small marks, or slight grid wear with no sagging or staining.
|  |  |  | Minor Repair | Local tile staining, small cracks, loose grid parts, or minor moisture damage needing repair.
|  |  |  | Major Repair | Widespread sagging, staining, warped grid, or major moisture damage reducing performance.
|  |  |  | Replacement | Severe deterioration, major leaks, collapsed sections, mold, or instability requiring full replacement.
D. SERVICES | Elevators & Lifts | D1010 | Traction elevators, hydraulic elevators, machine-room-less elevators; elevator cars, doors, hoistways, guide rails, controllers; elevator machines, motors, drives, brakes, sheaves; hydraulic pumps, cylinders, valves, fluid reservoirs; elevator cabs, panels, flooring, lighting, handrails; hoistway doors, frames, operators, interlocks, safety edges; elevator pits, buffers, sumps, ladders; wheelchair lifts, platform lifts, stair lifts; elevator monitoring and control systems; emergency communication systems in cabs. | New | Elevators and lifts operate smoothly with no abnormal noise, vibration, leaks, or door issues.
|  |  |  | Routine Maintenance | Minor cosmetic wear or slight timing adjustments with no impact on reliability.
|  |  |  | Minor Repair | Intermittent door issues, small leveling problems, minor leaks, or worn components needing repair.
|  |  |  | Major Repair | Frequent shutdowns, major door failures, severe vibration, or control faults affecting safety.
|  |  |  | Replacement | Equipment failure, unsafe conditions, or non-functional systems requiring replacement or modernization.
| Domestic Water Distribution | D2010 | Cold water distribution piping, valves, fittings, hangers; domestic hot water distribution piping to fixtures; recirculation systems and pumps; mixing valves, tempering valves, pressure-reducing valves; backflow preventers, vacuum breakers, air gaps; water meters, flow meters; expansion tanks, pressure tanks; pipe insulation, heat tracing; hose bibbs, wall hydrants, frost-proof fixtures; point-of-use water heaters; water hammer arrestors; shut-off valves, balancing valves. | New | Domestic water piping, valves, and insulation are leak-free, corrosion-free, and maintain proper flow and pressure.
|  |  |  | Routine Maintenance | Minor insulation wear, slight corrosion, or small seepage with no performance impact.
|  |  |  | Minor Repair | Local leaks, degraded insulation, minor corrosion, or small pressure issues requiring repair.
|  |  |  | Major Repair | Significant corrosion, recurring leaks, damaged piping, or persistent pressure problems.
|  |  |  | Replacement | Widespread corrosion, major leaks, or piping failure requiring full system or segment replacement.
| Plumbing Fixtures | D2015 | Water closets, urinals, lavatories, sinks, service sinks, drinking fountains, water coolers, showers, bathtubs, eyewash stations, emergency showers, mop sinks, clinical sinks, surgical scrub sinks, faucets and trim, flush valves, mixing valves, faucet aerators, drain assemblies, traps, fixture supports and carriers, grab bars integral to fixture installation, fixture insulation and protective coverings. | New | Plumbing fixtures and carriers are secure, clean, leak-free, and fully operational with no cracks or corrosion.
|  |  |  | Routine Maintenance | Minor wear to handles, trim, gaskets, or seals with no leakage or performance issues.
|  |  |  | Minor Repair | Local leaks, loose mounts, worn seals, or minor fixture damage requiring repair.
|  |  |  | Major Repair | Frequent leaks, cracked fixtures, carrier failure, or malfunctioning valves reducing functionality.
|  |  |  | Replacement | Severe fixture or carrier damage, structural failure, or continuous leakage requiring full replacement.
| Sanitary Waste & Vent Systems | D2020 | Sanitary waste and soil piping including cast iron, PVC, ABS, copper, stainless steel systems; horizontal and vertical stacks, branches, fixture arms; vent piping systems including vent stacks, branch vents, relief vents, stack vents, roof penetrations for vents; cleanouts, traps except fixture P-traps, adapters, hangers, anchors; waste/vent serving toilets, sinks, showers, floor drains, kitchen drains; grease waste piping inside building; sumps and ejectors for sanitary lift; condensate drains to sanitary. | New | Sanitary piping and vents are leak-free, corrosion-free, unobstructed, and draining properly with no odors or staining.
|  |  |  | Routine Maintenance | Minor surface corrosion or small cleanout needs with no leaks or flow issues.
|  |  |  | Minor Repair | Local leaks, small blockages, slow drains, or minor corrosion requiring cleaning or repair.
|  |  |  | Major Repair | Significant blockage, recurring backups, cracked piping, or widespread leaks affecting drainage.
|  |  |  | Replacement | Major corrosion, pipe failure, breaks, or unsafe conditions requiring full system replacement.
| Facility Fuel Systems | D3010 | Fuel distribution piping within building including natural gas, propane, fuel-oil piping; mains, risers, branches, valves, regulators; fuel storage systems located inside building including day tanks, interior fuel-oil tanks, transfer pumps, leak detection; pressure regulation and metering; fuel-oil handling equipment including strainers, filters, pumps, duplex pump sets, fuel polishers; emergency shutoff valves, solenoid valves, excess-flow devices; heat tracing and insulation on fuel-oil piping. | New | Fuel tanks, piping, valves, and controls are secure, clean, leak-free, and operating safely with proper containment.
|  |  |  | Routine Maintenance | Minor rust, light insulation wear, or slight gasket aging with no leaks.
|  |  |  | Minor Repair | Local corrosion, small seepage, damaged insulation, or minor valve issues needing repair.
|  |  |  | Major Repair | Significant corrosion, leaking components, failed containment, or faulty controls reducing safety.
|  |  |  | Replacement | Major tank or piping failure, severe corrosion, or unsafe leaks requiring full replacement.
| Heating Systems | D3020 | Boilers for heating including fire-tube, water-tube, electric, condensing; burners and combustion controls, fuel trains, safety valves; boiler feedwater systems, chemical treatment, blowdown equipment; heat exchangers for hot water or steam systems; thermal fluid heaters, heat transfer systems; radiant heating boilers; unit heaters, cabinet heaters, infrared heaters; duct furnaces and make-up air heaters; boiler room piping, valves, pumps, expansion tanks; boiler flues, stacks, combustion air systems. | New | Heating equipment operates smoothly with no leaks, corrosion, noise, or performance issues; all components function properly.
|  |  |  | Routine Maintenance | Minor gasket wear, slight corrosion, or small adjustment needs with no performance loss.
|  |  |  | Minor Repair | Local leaks, minor insulation damage, pump vibration, or reduced output requiring repair.
|  |  |  | Major Repair | Significant leaks, burner issues, exchanger problems, or major corrosion affecting safety or function.
|  |  |  | Replacement | Severe heating equipment failure, unsafe combustion, or major deterioration requiring replacement.
| Cooling Systems | D3030 | Chillers including water-cooled, air-cooled, absorption, centrifugal, screw, scroll; cooling towers, evaporative condensers, fluid coolers, adiabatic coolers; condenser water pumps, chemical treatment systems, cooling tower basins and sumps; chilled water pumps, primary and secondary loops; heat exchangers for chilled water systems; free cooling systems, economizer loops, waterside economizers; glycol systems for freeze protection; thermal storage systems, ice storage, chilled water storage. | New | Cooling systems run efficiently with no refrigerant leaks, corrosion, coil fouling, vibration, or water-treatment issues.
|  |  |  | Routine Maintenance | Minor coil debris, light corrosion, or slight noise increases with no loss of cooling.
|  |  |  | Minor Repair | Local refrigerant leaks, minor corrosion, degraded insulation, or small vibration issues needing repair.
|  |  |  | Major Repair | Major refrigerant loss, coil fouling, failing fans/compressors, or significant corrosion impairing cooling.
|  |  |  | Replacement | Severe system failure such as non-functional compressors, major structural deterioration, or unsafe operation requiring replacement.
| HVAC Air Distribution | D3041 | Ductwork including supply, return, exhaust, outside air ducts; duct insulation, liners, vapor barriers; air handling units, fans, filters, heating/cooling coils, dampers within units; VAV boxes, reheat coils, fan-powered boxes, mixing boxes; exhaust fans, supply fans, return fans; duct-mounted fire dampers, smoke dampers, combination dampers; diffusers, registers, grilles, louvers; duct access doors, volume dampers, balancing dampers, duct supports and hangers. | New | Air handlers, fans, ducts, dampers, and insulation are clean, sealed, balanced, and operating quietly with no leaks or damage.
|  |  |  | Routine Maintenance | Minor dust, light belt wear, or slight damper stiffness with no airflow issues.
|  |  |  | Minor Repair | Local duct leaks, worn belts, noisy fans, insulation damage, or minor corrosion needing repair.
|  |  |  | Major Repair | Major leakage, failing motors, damaged casings, severe corrosion, or major airflow imbalance.
|  |  |  | Replacement | Collapsed ducts, severely corroded equipment, failed fans, or non-functional AHUs requiring full replacement.
| HVAC Hydronic & Steam Distribution | D3042 | Hydronic distribution piping including hot water, chilled water, condenser water, glycol-solution piping; mains, risers, branches, drops to coils, radiators, unit heaters, fan-coils; fittings, unions, dielectric fittings, expansion loops, supports, hangers; steam and condensate distribution piping; low/medium-pressure steam to coils, heat exchangers, terminal units; condensate return piping, flash tanks, condensate pumps/receivers; steam traps, strainers, drip legs, air vents; distribution pumps, isolation valves, balancing valves, check valves, flow meters; expansion tanks, air separators, dirt separators; insulation and jacketing. | New | Hydronic and steam piping, valves, and insulation are intact, leak-free, and circulating properly with no corrosion or flow issues.
|  |  |  | Routine Maintenance | Minor insulation wear, light corrosion, or small valve seepage with no performance impact.
|  |  |  | Minor Repair | Local leaks, steam trap issues, minor corrosion, or degraded insulation requiring repair.
|  |  |  | Major Repair | Significant leaks, widespread corrosion, failed traps, or major flow issues impairing reliability.
|  |  |  | Replacement | Severe pipe failure, pervasive corrosion, major leaks, or unsafe operation requiring replacement.
| Terminal & Package Units | D3050 | Rooftop packaged units, split systems, heat pumps, mini-split systems, packaged terminal air conditioners (PTACs), water source heat pumps, fan coil units, unit ventilators, cabinet unit heaters, convectors, baseboard heaters, radiators, induction units, chilled beams, radiant panels, computer room air conditioning (CRAC) units, precision cooling units, self-contained units, through-wall units, condensing units, air-cooled condensers. | New | Terminal units (VAVs, FCUs, unit heaters, heat pumps, VRF units, PTACs) run smoothly with no leaks, noise, or condensation issues.
|  |  |  | Routine Maintenance | Minor filter wear, light coil dust, or slight vibration with no performance impact.
|  |  |  | Minor Repair | Local refrigerant leaks, minor coil corrosion, blower issues, or drainage problems needing repair.
|  |  |  | Major Repair | Major coil failure, refrigerant issues, failing motors, or widespread comfort problems.
|  |  |  | Replacement | Extensive deterioration, major mechanical failure, or unsafe operation requiring full unit replacement.
| HVAC Controls & Instrumentation | D3080 | Building automation systems (BAS) for HVAC, DDC controllers, control panels, sensors, thermostats, humidistats, pressure sensors, flow meters as control devices, actuators for dampers and valves, control valves for heating and cooling, variable frequency drives for pumps and fans, energy management systems, graphical user interfaces, networking and communication infrastructure for BAS, smoke control integration with fire alarm, start/stop scheduling and programming. | New | Controls, BAS components, sensors, and actuators are fully functional with accurate readings, stable communication, and no alarms.
|  |  |  | Routine Maintenance | Minor calibration drift, slight sensor wear, or small programming needs with no system impact.
|  |  |  | Minor Repair | Local sensor failures, minor actuator issues, loose wiring, or frequent overrides requiring repair.
|  |  |  | Major Repair | Widespread control faults, major actuator failures, network issues, or unstable BAS performance.
|  |  |  | Replacement | Obsolete, unsupported, or non-functional controls requiring major replacement or full BAS modernization.
| Other HVAC Systems & Equipment | D3090 | Dedicated outdoor-air systems (DOAS) when specialized treatment units; energy recovery systems including heat wheels, plate exchangers, run-around loops, ERV/HRV; specialty ventilation/treatment systems including dehumidification units, humidifiers, steam humidifiers, condensate treatment; environmental/process HVAC including CRAC/CRAH units, precision environmental control, clean-room units, process cooling/heating; specialized heating/cooling support like glycol mixing packages, heat-recovery chillers; infrared radiant heating systems, large industrial/warehouse radiant arrays; HEPA/ULPA filtration banks, activated carbon scrubbing; specialty pumps or packaged systems. | New | Specialized HVAC systems (lab exhaust, ERVs, humidification, critical cooling) operate smoothly with no leaks, corrosion, alarms, or airflow issues.
|  |  |  | Routine Maintenance | Minor filter wear, light debris, or small vibration with no performance impact.
|  |  |  | Minor Repair | Local corrosion, small leaks, minor sensor faults, or filtration issues requiring repair.
|  |  |  | Major Repair | Major airflow imbalance, failing motors, severe corrosion, or persistent alarms affecting critical spaces.
|  |  |  | Replacement | System failure, unsafe exhaust, severe corrosion, or non-functional units requiring full replacement.
| Fire Suppression Systems | D4010 | Wet pipe sprinkler systems, dry pipe systems, pre-action systems, deluge systems; sprinkler heads, piping, fittings, hangers, braces; fire department connections, post indicator valves, OS&Y valves, control valves; flow switches, tamper switches, pressure switches; fire pumps, jockey pumps, controllers, pressure maintenance; standpipes and hose connections; sprinkler room piping, drains, test connections; antifreeze systems in sprinkler piping; water storage tanks dedicated to fire protection; standpipe systems, hose valves, roof manifolds; kitchen hood fire suppression; clean agent suppression including FM-200, Novec, CO2; foam suppression. | New | Fire suppression piping, heads, valves, pumps, and components are intact, leak-free, unobstructed, and fully functional.
|  |  |  | Routine Maintenance | Minor corrosion, dust buildup, or slight valve stiffness with no leaks or flow issues.
|  |  |  | Minor Repair | Local leaks, corroded fittings, damaged heads, or pump issues requiring repair.
|  |  |  | Major Repair | Significant corrosion, recurring leaks, impaired pump operation, or system blockages.
|  |  |  | Replacement | Extensive corrosion, major leaks, failed pumps, or unsafe system conditions requiring full replacement.
| Electrical Service & Switchgear | D5010 | Electrical service entrance, main switchboards, switchgear, main service transformers, meter centers, utility metering; main distribution equipment, main disconnects, service protection devices; grounding systems, ground rods, grounding electrodes, bonding; surge protection devices at service entrance; emergency and standby generators, automatic transfer switches, generator fuel systems; central uninterruptible power supply (UPS) systems, battery backup systems; generator control panels, paralleling switchgear. | New | Electrical service gear, switchboards, meters, and grounding are secure, clean, and free of overheating, corrosion, or insulation damage.
|  |  |  | Routine Maintenance | Minor oxidation or labeling issues with no safety or performance concerns.
|  |  |  | Minor Repair | Local overheating, loose lugs, minor insulation damage, or limited breaker malfunction requiring repair.
|  |  |  | Major Repair | Major corrosion, repeated breaker trips, damaged bus components, or grounding issues.
|  |  |  | Replacement | Severe damage, arc-flash risk, non-functional gear, or major corrosion requiring full replacement.
| Electrical Distribution | D5020 | Distribution panels and subpanels including panelboards, load centers, lighting panels, equipment panels; feeder conductors and raceways from main switchgear to distribution panels or large equipment; dry-type interior transformers including step-down or isolation transformers; bus systems including bus ducts, busways, vertical bus risers; protective devices including breakers, fuses, relays; metering, monitoring, and power quality devices; motor control centers serving multiple loads; cable trays, wireways, conduit, enclosures, supports for distribution feeders. | New | Distribution panels, feeders, transformers, busways, and MCCs operate safely with no overheating, corrosion, or insulation issues.
|  |  |  | Routine Maintenance | Minor wear, dust buildup, or small labeling gaps with no operational impact.
|  |  |  | Minor Repair | Local overheating, worn breakers, loose lugs, or minor insulation failure requiring repair.
|  |  |  | Major Repair | Failing transformers, major corrosion, misaligned busways, or widespread overheating.
|  |  |  | Replacement | Major insulation failure, non-functional MCCs, extensive corrosion, or unsafe conditions requiring replacement.
| General Purpose Electrical Power | D5030 | Branch-circuit wiring including copper/aluminum conductors in conduit, cable assemblies (MC/AC), flexible conduit; receptacles and device outlets including standard duplex outlets, GFCI/AFCI receptacles, specialty outlet types; lighting branch circuits (wiring only); small equipment feeds not requiring dedicated distribution panels; junction boxes, device boxes, cover plates; dedicated circuits for small appliances or equipment; permanent raised-access floor systems with integrated power distribution; wiring to plug-connected modular furniture when building-managed. | New | Branch wiring, devices, and outlets are intact, secure, and free of overheating, discoloration, or damage; all circuits operate correctly.
|  |  |  | Routine Maintenance | Minor device wear, slight discoloration, or small labeling issues with no performance impact.
|  |  |  | Minor Repair | Loose outlets, minor insulation wear, damaged plates, or localized wiring issues requiring repair.
|  |  |  | Major Repair | Overheating devices, repeated trips, damaged junction boxes, or widespread outlet failures.
|  |  |  | Replacement | Severe insulation failure, major wiring damage, pervasive overheating, or unsafe circuits requiring replacement.
| Lighting | D5040 | Interior lighting fixtures, lamps, ballasts, LED drivers; exterior building-mounted lighting; exit signs, emergency lighting, egress path lighting; lighting controls including switches, dimmers, occupancy sensors, photocells, time clocks, relay panels; architectural lighting, decorative fixtures; task lighting and under-cabinet lighting; specialized lighting for sports facilities, stages, or auditoriums; lighting poles and standards attached to building; fixture mounting hardware, supports, canopies; lighting branch circuit wiring when dedicated to lighting control. | New | Lighting systems, including fixtures, drivers, controls, and emergency units, operate fully with no flicker, damage, or moisture intrusion.
|  |  |  | Routine Maintenance | Minor lens wear, slight discoloration, or isolated lamp/driver issues with no system impact.
|  |  |  | Minor Repair | Local fixture failures, damaged housings, loose mounts, or minor water intrusion requiring repair.
|  |  |  | Major Repair | Major outages, widespread corrosion, repeated driver failures, or compromised emergency lighting.
|  |  |  | Replacement | Severe fixture deterioration, non-functional emergency lighting, or unsafe conditions requiring full replacement.
| Communication Systems | D6010 | Telephone systems, voice cabling, telecom rooms, patch panels, terminal blocks; data networking infrastructure, fiber optics, copper cabling, network switches, racks, cabinets; structured cabling systems; intercom and paging systems, public address systems, mass notification; clock and program bell systems; distributed antenna systems (DAS); audiovisual infrastructure cabling, display connections; cable pathways, conduit, cable trays for low-voltage systems; grounding and bonding for communications systems; communication outlets and jacks. | New | Communications cabling, racks, patch panels, outlets, and PA/clock systems are neat, supported, labeled, and fully functional.
|  |  |  | Routine Maintenance | Minor cable wear, slight labeling gaps, or small connector issues with no performance impact.
|  |  |  | Minor Repair | Damaged cabling, loose terminations, minor equipment issues, or localized PA/clock failures requiring repair.
|  |  |  | Major Repair | Significant cabling faults, widespread connectivity problems, or major equipment failures.
|  |  |  | Replacement | Obsolete or non-functional systems, major cabling failure, or unsafe conditions requiring full replacement.
| Access Control & Intrusion Detection | D7010 | Card access systems, card readers, proximity readers, biometric readers; electronic locks, electric strikes, magnetic locks, electrified hardware; access control panels, controllers, field panels; intrusion detection sensors, motion detectors, door contacts, glass break sensors; intrusion alarm panels, keypads, annunciators; security system cabling, power supplies, backup batteries; credential management systems, access control software; perimeter detection systems, duress alarms, panic buttons; integration with video surveillance for event verification. | New | Access control and intrusion systems, including readers, locks, sensors, and panels, operate correctly with no wiring or device faults.
|  |  |  | Routine Maintenance | Minor reader wear, small alignment issues, or slight panel battery aging with no system faults.
|  |  |  | Minor Repair | Local sensor failures, intermittent reader issues, loose wiring, or minor controller faults requiring repair.
|  |  |  | Major Repair | Widespread device failure, major controller issues, recurring false alarms, or unreliable locking.
|  |  |  | Replacement | Non-functional controllers, severe wiring damage, or compromised security requiring system replacement.
| Video Surveillance | D7020 | Video surveillance cameras including fixed, PTZ, dome cameras; network video recorders (NVR), digital video recorders (DVR), video management systems; camera mounting hardware, housings, enclosures, poles for cameras; video cabling, fiber optics, network infrastructure for cameras; monitors and displays for viewing surveillance; video analytics software, motion detection, facial recognition integration; camera power supplies, PoE switches, backup power for surveillance; outdoor cameras with weatherproof housings, infrared night vision. | New | Cameras, NVRs, VMS, cabling, and monitors are fully functional with clear images, stable recording, and no housing or wiring issues.
|  |  |  | Routine Maintenance | Minor lens smudges, light wear, or small mounting adjustments with no image or recording impact.
|  |  |  | Minor Repair | Local camera failures, damaged housings, loose mounts, minor cabling issues, or small storage faults requiring repair.
|  |  |  | Major Repair | Major image loss, multiple device failures, VMS/NVR faults, or damaged exterior units affecting reliability.
|  |  |  | Replacement | System-wide failure, non-functional recording, major cabling deterioration, or unsafe equipment requiring replacement.
| Fire Detection & Alarm | D7050 | Fire alarm control panels, annunciators, remote stations; smoke detectors, heat detectors, flame detectors, duct detectors; manual pull stations, fire alarm horns, strobes, speakers for voice evacuation; notification appliances, visual and audible devices; sprinkler flow switches, tamper switches, valve supervision; fire alarm cabling, conduit, backboxes, mounting hardware; addressable and conventional fire alarm systems; mass notification integration; elevator recall and HVAC shutdown integration; fire fighter phones, communication systems; emergency voice alarm communication systems. | New | Panels, detectors, pull stations, NAC devices, and wiring function correctly with no trouble signals, false alarms, or damage.
|  |  |  | Routine Maintenance | Minor dust buildup, slight aging, or labeling gaps with no impact on detection or notification.
|  |  |  | Minor Repair | Local detector failures, intermittent troubles, damaged devices, or loose wiring requiring repair.
|  |  |  | Major Repair | Widespread detector faults, recurring false alarms, wiring degradation, or major panel issues.
|  |  |  | Replacement | System failure, obsolete components, non-functional devices, or unsafe conditions requiring replacement.
E. EQUIPMENT & FURNISHINGS | Detention Equipment | E1040 | Detention doors and frames with security glazing, tamper-proof hardware, electronic locks; security grilles, gates, sallyports; detention window systems with security glazing; security screens and partitions, including bullet-resistant assemblies; detention-grade plumbing fixtures that are tamper-proof; fixed detention furniture including bunks, desks, stools, benches securely anchored; security lighting fixtures with vandal-resistant covers; padded cell components and protective wall systems; detention cell fronts, bars, mesh. | New | Detention doors, locks, glazing, partitions, and fixed furniture are secure, aligned, tamper-resistant, and free of corrosion or damage.
|  |  |  | Routine Maintenance | Minor wear, small hardware adjustments, or light surface corrosion with no loss of security.
|  |  |  | Minor Repair | Local damage such as loose fasteners, glazing scratches, or minor hardware faults requiring repair.
|  |  |  | Major Repair | Significant deformation, locking failures, corrosion, or tampering damage affecting security.
|  |  |  | Replacement | Severe structural failure, major lock malfunction, or compromised security requiring full replacement.
| Fixed Furnishings | E2010 | Built-in casework and millwork including base cabinets, wall cabinets, lab casework, countertops, vanities; fixed shelving, bookcases, display cases; fixed seating and benches in auditoriums, lecture halls, stadium seating, built-in benches and booths; service counters, transaction desks, reception desks, service windows; fixed work surfaces, integrated desks, instructional stations, workstations; built-in closets, cubbies, locker alcoves; fixed display boards with integrated casework. | New | Casework, shelving, countertops, and built-ins are secure, intact, clean, and free of delamination, warping, or structural damage.
|  |  |  | Routine Maintenance | Minor surface wear, slight hardware looseness, or small finish defects with no functional issues.
|  |  |  | Minor Repair | Local delamination, damaged hardware, small structural defects, or minor moisture damage requiring repair.
|  |  |  | Major Repair | Widespread deterioration, major delamination, failing supports, or warped components reducing function.
|  |  |  | Replacement | Extensive damage, severe structural failure, or unusable built-ins requiring full replacement.
F. SPECIAL CONST. | Swimming Pool Systems | F1050 | Pool vessel and structure including concrete shells, liners, structural walls, gutters, surge tanks, integral waterproofing, tile finishes, pool plaster, expansion joints; water circulation systems with pumps, strainers, flow meters, valves, fittings, circulation piping, skimmers, gutters, return inlets, main drains; filtration systems including sand, DE, or cartridge filters, backwash valves and piping; pool heating systems; chemical treatment systems; deck drains and coatings; handrails, ladders, accessibility lifts. | New | Pool systems, equipment, piping, and surfaces are clean, leak-free, and operating with proper flow, heating, and chemical balance.
|  |  |  | Routine Maintenance | Minor wear, light debris, small gasket aging, or slight pump noise with no leaks or performance issues.
|  |  |  | Minor Repair | Local leaks, minor equipment faults, small surface damage, or reduced filtration requiring repair.
|  |  |  | Major Repair | Significant leaks, pump or heater failures, corrosion, filtration issues, or major surface deterioration.
|  |  |  | Replacement | Severe equipment failure, major piping damage, unsafe water conditions, or extensive surface failure requiring replacement.